## Slide 1: Cooling Process to avoid frosting on the surface of the KAGRA Test Mass and ….
Nobuhiro KIMURA
Institute for Cosmic Ray Research
The University of Tokyo
On behalf of the KAGRA cryogenic group
External Review for KAGRA Cooling Process to avoid Frosting 20/July/2021

## Slide 2
Contents
  Objective of the external review
  Defrosting experiment using KAGRA cryostat
  Proposal of the KAGRA cooling scenario for O4
  Enhancement plan to avoid frosting

## Slide 3
  Objective of this external review is
    “In order to avoid frosting on the surface of the test mass, this review confirms whether there are any remaining issues with the proposed cooling scenario for the test mass.”

## Slide 4
  Outline
    Purpose of the defrosting experiment
    Example of frosted view ports
    Cooling scenario examined to avoid frosting
    Result of cooling characteristics of the cryostat
    Residual gas measurement during the cooling
    Performance defrost heaters
  Summary of experiment
Defrosting experiment using KAGRA cryostat

## Slide 5
1. Determine the cooling process for Test Mass avoid frosting
Including confirmation of the occurrence of frosting on the test mass or view ports under the condition of leak rate <10^-10Pam^-3/s).
(Leakage of KAGRA specification is not >10^-10Pam^-3/s).)
2. Measurement of partial pressure of residual gas during cooling
Identification of frosting components.
It was assumed that frost was formed by frosting of O2, N2 and H2O.
3.Defrosting experiment by defrost heaters
Feasibility study of defrosting heaters.
(If no frost adheres during experiment, check the temperature profile by defrost heater.)
    Purpose of the defrosting experiment

## Slide 6: Example of frosted view ports
TM oplev light source side
TM oplev QPD side
Photos show examples of the frosting on the surface of view ports with vacuum leak at TM temperature of ~25K. (@EXC 2020/08)
It was assumed that frost was formed by frosting of O2, N2 or H2O.
    Frosting
Frosting on the surface of the test mass and there is a serious problem at the KAGRA.
In order to find a way to cool the test mass down to ~20 K while preventing frosting, KAGRA cryogenic subgroup have conducted the cooling experiment using the KAGRA cryostat.

## Slide 7: KAGRA cryogenic system
Duct Shield
Duct Shield
Test mass
Cryo-cooler units
View ports
Outer radiation shield
Inner radiation shield
Structural view of KAGRA Cryostat with shield ducts
Notes: KAGRA cryostat consist of one main cryostat and two cryo-duct shields.
The main cryostat has a inner and a outer radiation shield.
Cryo-payload with Test Mass is in the inner radiation shield.
View ports for Opleve are attached inner and outer radiation shield.

## Slide 8: Cryo-cooler layout
Four cryocooler units per one cryostat
Main Beam
Inner shield
cooling
Cooling
Cryo-Payload
Duct Shield
400kW
Cryostat
Outer radiation shield
Inner radiation shield
two units
Pulse Tube type Cryo-cooler (PTC) with Vibration reduction
two units
2 units for cooling cryo-payload
2 units for cooling inner shield
4 units for cooling outer shield
300K
Radiation
Baffles
Cryo-payload
cooling

## Slide 9: Temperature distribution and internal pressure of the KAGRA cryostat after cooling
Duct Shield
= 90 ~ 125 K
Duct Shield
= 90 ~ 125 K
Test mass
= 23 K
Outer radiation shield
=~100 K
Inner radiation shield
= ~15 K
Internal pressure = 5.8 x 10^-6 Pa

## Slide 10: Cooling scenario examined to avoid frosting
Fundamental features of the cooling method:
Avoiding frost on the test mass by stepwise adsorption of residual gas components on the radiation shield surface
Step 1
Step 2
Step 3
Final
Step
21 days
11 days
24 days
Goal
10 days
Vacuum pumping
Internal pressure
< 10^-4 Pa
No leakage
> 10^-10 Pam^3/s
Cooling down
duct shields
Radiation Temp.
90 K ~ 150 K
Trap H2O
Cooling down
internal shields
Radiation Temp.
20 K ~ 30K
Trap O2 and N2
Cooling down
Test
Mass
TTM=~20 K
It takes 76 days in total to cool down Test Mass

## Slide 11: Cooling scenario examined to avoid frosting
Fundamental features of the proposed cooling method:
Avoiding frost on the test mass by stepwise adsorption of residual gas components on the radiation shield surface
Step 1: Start vacuum pumping.
Wait inner pressure shall be lower than ~10^-4 Pa.
  It will take 21 days including 3 days of vacuum leak test .
  Leak test should be satisfied KAGRA specification which are no leakage > 1x10^-10 Pam^3/sec.

## Slide 12
> 1x10-4 Pa
Evacuated by vacuum pumps
Step 1: Evacuation by vacuum pumps

## Slide 13
Step 2: Turn on duct shield cryocoolers to trap H2O on the surface of duct shield.
  Wait surface temperature of duct shield should be lower than 130 K. It will take 11 days.
Step 3: Turn on two cryocooler for radiation shields to trap N2 on the surface of inner shield.
  The mirror is cooled by radiation from the inner shield.
  Wait surface temperature of inner shield should be lower than 20 K.
  It will take 24 days after turning on the coolers.

## Slide 14
Touter > 130 K
> 1x10-6 Pa
Step 2:Trap H2O by duct & outer shields

## Slide 15
Step 2: Turn on duct shield cryocoolers to trap H2O on the surface of duct shield.
  Wait surface temperature of duct shield should be lower than 130 K. It will take 11 days.
Step 3: Turn on two cryocooler for radiation shields to trap N2 on the surface of inner shield.
  The mirror is cooled by radiation from the inner shield.
  Wait surface temperature of inner shield should be lower than 20 K.
  It will take 24 days after turning on the coolers.

## Slide 16
20 < Tinner
< 1x10-6 Pa
Step 3: Trap O2 & N2 by inner shield

## Slide 17
Final Step:
  Turn on two cryo-coolers for payload.
  It will take 10 days after switched on the coolers to reach steady state condition of mirror temperature.

## Slide 18
  Outline
    Purpose of the defrosting experiment
    Example of frosted view ports
    Cooling scenario examined to avoid frosting
    Result of cooling characteristics of the cryostat
    Performance defrost heaters
    Residual gas measurement during the cooling
  Summary of experiment
Defrosting experiment using KAGRA cryostat

## Slide 19
Two turbo molecule pumps “ON”,
when P < 10 Pa
One root pump “ON”
Temperature dependence of internal pressure
> 140 K
Two duct shield cooler “ON”,
when P ~10^-4 Pa
\
> 30 K
Two cryostat shield cooler “ON”, Tduct=150~200 K, TTM ~ 230 K
Pcryo= ~5.8 x 10^-6 Pa
Two payload cooler “ON”, Tinner < 30 K,
TTM > 150 K

## Slide 20
  Outline
    Purpose of the defrosting experiment
    Example of frosted view ports
    Cooling scenario examined to avoid frosting
    Result of cooling characteristics of the cryostat
    Residual gas measurement during the cooling
    Performance defrost heaters
  Summary of experiment
Defrosting experiment using KAGRA cryostat

## Slide 21
N2
Trap by inner shield
~20 K
H2O
Trap by duct shield
~130 K
Temperature dependence of H2O and N2

## Slide 22
O2
Temperature dependence of Q-mass

## Slide 23
  Outline
    Purpose of the defrosting experiment
    Example of frosted view ports
    Cooling scenario examined to avoid frosting
    Result of cooling characteristics of the cryostat
    Residual gas measurement during the cooling
    Performance defrost heaters
  Summary of experiment
Defrosting experiment using KAGRA cryostat

## Slide 24: Defrost heater layout
A small heater was attached on IM for defrosting mirror surface.
Two calibration heaters were equipped with
the top of inner radiation shield.
One defrost heater was attached on view port.
Three kinds of heaters for defrosting were installed in this experiment.
Image of defrost heater

## Slide 25
Defrost heater
“ON”
Qdh=~5 W
Characteristics of heat input response
IM heater “ON”, QIM=2.5 W
~two days
TTM=~75 K
Inner top cal heater “ON”, QTh=~31 W
Inner Top cal heater “OFF”
~two days
Tinner shield=~45 K

## Slide 26
Frosting on the surface of view ports were not appeared during the experiment!
It can be assumed frosting on the surface of Test Mass was not appeared visually.
Following items were confirmed with the experiment;
  Proposed cooling scenario can avoid frosting for O4.
  Calibration heaters worked well as defrost heaters for view ports on the inner shield. To defrost the view ports on inner shield, it will take 1 days to warm up to ~50 K (above O2 vapor temperature of 48 K at 1x10^-5 Pa) , and 1 days to re-cool down to ~20 K.
  Heater attached on the IM worked well as defrost heater for mirror.
  To defrost the mirror, it will take 1 days to warm up to ~70 K,
  (above N2 vapor temperature of 53 K at 1x10^-3 Pa) , and 1 days to re-cool down to ~20 K.
  Partial pressure measurement of residual gas at each temperature was performed, and confirmed frosting components.
Summary of experiment -1/2-

## Slide 27
Lessons learned
Best effort for minimizing vacuum leak
Mitigation of frosting
  Four steps cooling method.
  Defrosting by heaters, when frost is occurred.
  Confirmation no leakage > 10^-10 Pam^3/sec.
  Check continuous measurement of residual gas components in the all of vacuum chambers.
Summary of experiment -2/2-

## Slide 28
KAGRA test masses will be cooled down with the same cooling method as same as the defrosting experiments.
It will take two and half months to reach ~20 K.
Use the defrost heater to defrosting, when it appear on the surface of the test mass or view port.
It needs two days to defrost.
Reinforce of leak testing to satisfy KAGRA's required specifications < 1x10^-10 Pam^3/s for all of vacuum chambers
  Proposal of the KAGRA cooling scenario for O4

## Slide 29
Enhance pumping capacity by increasing the number of vacuum pumps.
Especially around the cryostat, to reduce the achieved pressure as much as possible.
Add process gas monitor, to realize continuous measurement of residual gas components in the vacuum chambers including PR, SR, BS and so on.
Enhancement plan to avoid frosting

## Slide 30
Plan for increasing the number of vacuum pumps to enhance pumping capacity by
EYC
IYC
EXC
IXV
BS
PRM
PR3
PR2
SRM
SR3
SR2
OMC
MCF
MCE
3000 m
IXA
EXA
IFI
EYT
EXT
IYA
EYA
MC : Mode Cleaner
BS : Beam Splitter
IXA, EXA, IYA, EYA : Auxiliary optical baffle
EXT, EYT : Transmitting telescope
IXC, EXC, IYC, EYC : Cryogenic Mirror
IXV, EXV, IYV, EYV : Vibration Isolation (2nd story)
GV: Gate valve
IMM
OMMT
茂住側
佐古西側
跡津側
GVitmx
GVetmx
GVitmy
GVetmy
GVmc
GVbsx
GVbsy
EYV
IYV
EXV
IXC
TMP
IP
solid mark = already installed
blank mark = additively to be installed
14 of ion pumps
8 of turbo-molecular pumps
[10]
[13]
[6]
[3]
[5]
[28]
[29]
[30]
[31]
[32]
[39]
[37]
[36]
[38]
[34]
[26]
[27]
[41]
[40]
[42]
[43]
[44]
[45]
[14]
[9]
[2]
[1]
[11]
[12]
[15]
[21-25]
[33]
[35]
[16-20]
[7]
[8]

## Slide 31: Appendix

## Slide 32
Beam duct
14m
Main mirror parts
Cryostat with four cryocoolers
Overview of KAGRA Cryogenics system
Cryo shield ducts
in order to terminate
300 K radiation
Vibration isolation system
at room temperature

## Slide 33: Structure of KAGRA Cryostat
Seismic Attenuation System (SAS)
Duct Shield
Four Cryocooler Units
Main Laser Beam
Radiation Shields
4.3 m
2.6m
Cryogenic Payload
Sapphire Mirror
(-alumina crystal)
S. Koike
View Ports
Stainless steel t=20mm
Diameter 2.4 m
Height ~4.3 m
M ~ 12 ton
Cold Mass:
8K shield ~455 kg
80 K shield ~590 kg
Cryocoolers
Pulse tube, 60Hz
0.9 W at 4K (2nd)
36 W at 50K (1st)

## Slide 34: 1x10-3 Pa → ~-220 ℃（~53 K）
State diagrams of O2 and N2
Gas
1x10-5 Pa → ~-225 ℃（~48 K）
O2
super critical
Liquid
Solid
Pressure (MPa absolute)
Gas
Boiling point:-182.96 C
Temperature (℃)
N2
Pressure (MPa absolute)
Solid
Liquid
super critical
Gas
Boiling point:-147.1 C
Temperature (℃)

## Slide 35
Temperature dependence of Q-mass